{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["Sheet1"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":33,"n_cols":9,"rows_kept":33,"merged":[[0,0,0,8],[1,0,2,0],[1,1,2,1],[1,2,1,3],[1,4,2,4],[1,5,2,5],[1,6,2,6],[1,7,2,7],[1,8,2,8],[3,1,11,1],[4,7,8,7],[10,7,18,7],[12,1,18,1],[19,1,26,1],[19,7,26,7],[27,0,27,8],[29,0,29,8],[30,0,30,8],[31,0,31,5],[32,0,32,5],[32,6,32,7]],"flags":["formulas_cached_only"]}
["2023年度第二批管材及管件采购项目询价报价表"]
["序号","材料名称","规格型号",null,"技术参数","单位","报价（元）","防腐要求","备注"]
[null,null,"公称直径（DN）","外径（D）"]
[1,"焊接钢管","DN1200*12  Q235B","D1220×12  Q235B","普碳钢板卷管","t",null,"管道内壁防腐（二底二面）先刷GZ-2底漆2道，面漆2道，2道底漆干膜厚度大于60um，2道面漆干膜厚度大于60um，总干膜厚度大于120um。\n架空管道外壁防腐（二布六油）先刷环氧煤沥青底漆二道，缠绕玻璃纤维布一层，再涂底漆二道，再缠绕玻璃纤维布一层，再涂面漆二道。干膜厚度大于520um。","（架空敷设）"]
[2,null,"DN1200*12  Q235B","D1220×12  Q235B","普碳钢板卷管","t",null,"管道内壁防腐（二底二面）先刷GZ-2底漆2道，面漆2道，2道底漆干膜厚度大于60um，2道面漆干膜厚度大于60um，总干膜厚度大于120um。\n埋地管道外壁防腐（二布四油）先刷环氧煤沥青底漆一道，缠绕玻璃纤维布一层，再涂底漆一道，再缠绕玻璃纤维布一层，再涂面漆二道。干膜厚度大于400um。","埋地"]
[3,null,"DN1400*14  Q235B","D1420*14  Q235B","普碳钢板卷管","t",null,null,"埋地"]
[4,null,"DN1000*10  Q235B","D1020*10  Q235B","普碳钢板卷管","t",null,null,"埋地"]
[5,null,"DN600*8   Q235B","D630*8  Q235B","普碳钢板卷管","t",null,null,"埋地"]
[6,null,"DN200*6 Q235B","D273*6 Q235B","普碳钢板卷管","t",null,null,"埋地"]
[7,null,"DN1400*18  Q345","D1420*18  Q345","普碳钢板卷管","t",null,"管道内壁防腐（二底二面）先刷GZ-2底漆2道，面漆2道，2道底漆干膜厚度大于60um，2道面漆干膜厚度大于60um，总干膜厚度大于120um。\n熔结环氧粉末外防腐层的涂装质量标准按《熔融结合环氧粉末涂料的防腐蚀涂装》（GB/T18593-2001)执行，厚度为大于400um。","顶管"]
[8,null,"异径管DN1400×DN1200"," Q235B","普碳钢板卷管","个",null,"管道内壁防腐（二底二面）先刷GZ-2底漆2道，面漆2道，2道底漆干膜厚度大于60um，2道面漆干膜厚度大于60um，总干膜厚度大于120um。\n埋地管道外壁防腐（二布四油）先刷环氧煤沥青底漆一道，缠绕玻璃纤维布一层，再涂底漆一道，再缠绕玻璃纤维布一层，再涂面漆二道。干膜厚度大于400um。"]
[9,null,"异径管DN1400×DN1000"," Q235B","普碳钢板卷管","个"]
[10,"管件","三通\nDN1400×DN200"," Q235B","普碳钢板卷管","个"]
[11,null,"三通DN1400×DN1400"," Q235B","普碳钢板卷管","个"]
[12,null,"三通DN1200×DN1200"," Q235B","普碳钢板卷管","个"]
[13,null,"三通\nDN800×DN1000"," Q235B","普碳钢板卷管","个"]
[14,null,"三通DN1400×DN1000"," Q235B","普碳钢板卷管","个"]
[15,null,"排泥三通DN1400×DN600"," Q235B","普碳钢板卷管","个"]
[16,null,"法兰盘DN1000及DN1000法兰盲板"," Q235B","普碳钢板卷管","个"]
[17,"管件","排气三通DN1400×DN100"," Q235B","普碳钢板卷管","个",null,"管道内壁防腐（二底二面）先刷GZ-2底漆2道，面漆2道，2道底漆干膜厚度大于60um，2道面漆干膜厚度大于60um，总干膜厚度大于120um。\n埋地管道外壁防腐（二布四油）先刷环氧煤沥青底漆一道，缠绕玻璃纤维布一层，再涂底漆一道，再缠绕玻璃纤维布一层，再涂面漆二道。干膜厚度大于400um。"]
[18,null,"排气三通DN1400×DN150"," Q235B","普碳钢板卷管","个"]
[19,null,"11.25°水平钢制弯头，DN1400×14mm"," Q235B","普碳钢板卷管","个"]
[20,null,"22.5°水平钢制弯头，DN1400×14mm"," Q235B","普碳钢板卷管","个"]
[21,null,"30°水平钢制弯头，DN1400×14mm"," Q235B","普碳钢板卷管","个"]
[22,null,"45°水平钢制弯头，DN1400×14mm"," Q235B","普碳钢板卷管","个"]
[23,null,"60°水平钢制弯头，DN1400×14mm"," Q235B","普碳钢板卷管","个"]
[24,null,"90°水平钢制弯头，DN1400×14mm"," Q235B","普碳钢板卷管","个"]
["注：\n    1、报价范围包括：材料费（包含辅助、配套材料）、人工费、机械费、制作费、试验检测费、包装费、运杂费（包括装卸车费）、培训费、保险费、缺陷修复费、综合管理费、技术资料费、风险费、利润、各种税费、政策性文件规定费用等一切费用，即货物到达交货地点所发生的一切费用，具体以签订的合同条款为准。\n    2、各种规格钢管及管件的综合单价在合同有效期内若每批次管材每批次管材订单发出之日Q235B或Q345钢板材料单价波动范围不超过开标日前第六天Q235B或Q345钢板材料单价±5%（含±5%）的范围时不作调整；在合同有效期内若每批次管材每批次管材订单发出之日Q235B或Q345钢板材料单价波动范围超过开标日前第六天Q235B或Q345钢板材料单价±5%（不含±5%）的范围时，按以下方式调整相应材料单价价差后重新计价，具体调整方式如下：\n    (1) 超出+5%部分调整方式：\n某批次材料钢管及钢制管件结算时需调整单价价差＝每批次管材订单发出之日Q235B或Q345钢板材料单价－开标日前第六天Q235B或Q345钢板材料单价×1.05； \n    (2) 超出-5%部分调整方式：\n某批次材料钢管及钢制管件结算时需调整单价价差＝每批次管材订单发出之日Q235B或Q345钢板材料单价－开标日前第六天Q235B钢板材料单价×0.95； \n每批次管材订单发出之日Q235B钢板材料单价及开标日前第六天Q235B钢板材料单价均参照我的钢铁网（http://www.mysteel.com）广州市场相应钢厂钢板价格，双方对网上公布价格均不得有异议。\n    3、有关焊接钢管焊接工作面的防腐，供应商供货时，焊接钢管接口10cm范围内先不涂防腐层，待焊接工作完成后再涂防腐层，或供应商提供相应的防腐材料，由发包人自行完成焊接钢管防腐工作。\n    4、数量以具体工程实际需求为准，送货量月结80%，当年结算至97%，质量保证金3%完工一年后付清，具体以签订的合同条款为准。"]
[]
["供应商名称："]
["供应商地址："]
["联系人："]
["联系电话：",{"$nulls":5},"日期：2023年   月    日"]