{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["金属结构及机电设备"],"not_rendered":{"external_links":1,"defined_names":2},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"金属结构及机电设备","index":0,"n_rows":101,"n_cols":8,"rows_kept":101,"merged":[[0,0,0,1],[1,0,1,7],[94,1,94,2],[95,0,95,7],[96,0,96,5],[97,0,97,5],[98,0,98,5],[99,0,99,5],[100,0,100,5]],"flags":["formulas_cached_only"]}
["附件"]
["广东省惠州市中心城区防洪排涝综合治理工程（惠城区排涝站改造项目-老指挥部排涝站改造工程）金属结构及机电设备采购项目（第二次）询价报价表"]
["序号","材料名称","规格型号或指标、技术参数","单位","数量","单价报价（元）","合计（元）","备注"]
["一","水泵机组设备"]
["一）","新站水泵机电设备"]
[1,"单基础整体式轴流泵（自重6.5吨）","型号1000ZLDB-5.5，设计流量3.3m3/s，设计扬程5.3m，最高扬程7.16m，额定转速490r/min，叶片五轴联动数控加工，G1Cr18Ni9Ti材质，整体出厂吊装，水导轴承采用研龙PLYhRBR或赛龙Composite(Gm2401)轴承","台",{"v":2,"d":"2.00"}]
[2,"双法兰传力接头","型号VSSJAF，DN1000，0.6Mpa","个",{"v":2,"d":"2.00"}]
[3,"异步电动机(自重3吨)","YL450-12/280kw，280kW，380V，490r/min，F级，IP23，配套SKF轴承","台",{"v":2,"d":"2.00"}]
["二）","旧站水泵设备更换"]
[1,"更换旧站小泵组(自重2t)","单基础立式轴流泵350ZLBD-100，设计流量0.25m'/s，扬程2.35~6.7m，叶片角度-2，含配套高效率三相电机22kW，泵长度6.5m","台",{"v":2,"d":"2.00"}]
[2,"更换旧站低压无功补偿柜","补偿容量180kvar，800x800x2260m","套",{"v":1,"d":"1.00"}]
[3,"更换旧站小泵起动柜","软启动器30kW，800x800x1800m","套",{"v":2,"d":"2.00"}]
[4,"移动式潜污泵","WQ100-10-7.5，流量100㎡/h，扬程10m，功率7.5kW","台",{"v":1,"d":"1.00"}]
["二","金属结构设备"]
["一）","清污及起重设备"]
[1,"抓斗除污机","型式：液压耙斗钢丝绳卷扬式；安全工作负荷：1000kg；抓斗宽度：2.5m；栅条深度5m；栅条净距90mm；提升电机功率：5.5kW；提升速度10m/min；行走电机功率：2×0.75kW；行走速度：20m/min；液压泵功率：1.5kW；液压泵工作压力12Mpa，轨道32a工字钢，长度18m。带PLC控制箱(留100M以太网通讯口)。","台",{"v":1,"d":"1.00"}]
[2,"手推小车","储渣容积≥1.5m3，不锈钢304材质","个",{"v":1,"d":"1.00"}]
[3,"电动单梁起重机","LX-12t，起重量12吨，跨度5.0m，起升高度18m，起升速度8/0.8m/min，行走速度20m/min，工作级别A3，地面操作，I56a工字钢轨道，长度2×16m","台",{"v":1,"d":"1.00"}]
[4,"检修闸门电动葫芦","MD1-2x10t，起升高度12m，起升速度8/0.8m/min，行走速度20m/min，工作级别A3，地面操作","台",{"v":1,"d":"1.00"}]
[5,"泵站防洪闸门双吊点卷扬式启闭机(自重2.5t)","型号QPQ-2x10t，额定起重量2x10t，集中驱动方式，起升高度16m，吊点距见闸门结构图，起升速度2.3m/min，电动机功率11kW，卷筒直径400mn","台",{"v":2,"d":"2.00"}]
[6,"自排闸闸门双吊点卷扬式启闭机(自重3t)","型号QPQ-2x16t，额定起重量2x16t，集中驱动方式，起升高度16m，吊点距见闸门结构图，起升速度2.26m/min，电动机功率13kW，卷简直径400mmn","台",{"v":1,"d":"1.00"}]
["二）","闸门、拦污山、拍门设备"]
[1,"水闸防洪闸闸门7×5（1扇）","含防腐。钢表面采用喷砂(或抛丸)除锈，清除铁锈污物基体金属的表面清洁度等级不低于Sa2.5级。表面涂环氧富锌底漆一道不低于60μm，环氧云铁中间漆二道，每道80μm，最后涂氣化橡胶面漆一道80μm。","t",13.12]
[2,"闸门预埋件（1套）","含防腐。钢表面采用喷砂(或抛丸)除锈，清除铁锈污物基体金属的表面清洁度等级不低于Sa2.5级。表面涂环氧富锌底漆一道不低于60μm，环氧云铁中间漆二道，每道80μm，最后涂氣化橡胶面漆一道80μm。","t",3.74]
[3,"排涝站检修闸门3.44×4（1扇）","含防腐。钢表面采用喷砂(或抛丸)除锈，清除铁锈污物基体金属的表面清洁度等级不低于Sa2.5级。表面涂环氧富锌底漆一道不低于60μm，环氧云铁中间漆二道，每道80μm，最后涂氣化橡胶面漆一道80μm。","t",5.26]
[4,"闸门预埋件（2套）","含防腐。钢表面采用喷砂(或抛丸)除锈，清除铁锈污物基体金属的表面清洁度等级不低于Sa2.5级。表面涂环氧富锌底漆一道不低于60μm，环氧云铁中间漆二道，每道80μm，最后涂氣化橡胶面漆一道80μm。","t",8.38]
[5,"排涝站防洪闸门3.3×5（2扇）","含防腐。钢表面采用喷砂(或抛丸)除锈，清除铁锈污物基体金属的表面清洁度等级不低于Sa2.5级。表面涂环氧富锌底漆一道不低于60μm，环氧云铁中间漆二道，每道80μm，最后涂氣化橡胶面漆一道80μm。","t",12.72]
[6,"闸门预埋件（2套）","含防腐。钢表面采用喷砂(或抛丸)除锈，清除铁锈污物基体金属的表面清洁度等级不低于Sa2.5级。表面涂环氧富锌底漆一道不低于60μm，环氧云铁中间漆二道，每道80μm，最后涂氣化橡胶面漆一道80μm。","t",7.06]
[7,"老站拦污栅栅体（第一道）","组件及埋件均涂防锈漆及灰色环氧磁漆两遍。","t",6.83]
[8,"老站拦污栅预埋件（第一道）","组件及埋件均涂防锈漆及灰色环氧磁漆两遍。","t",2.31]
[9,"排涝站拦污栅栅体","组件及埋件均涂防锈漆及灰色环氧磁漆两遍。","t",4.13]
[10,"排涝站拦污栅预埋件","组件及埋件均涂防锈漆及灰色环氧磁漆两遍。","t",2.68]
[11,"节能型不锈钢自由侧翻式拍门（配缓冲装置）","孔口直径Φ1500mm，圆形单门，最大工作水头10.0m，阻力系数≤0.1，开启角度80°以上，水头损失≤0.04m，开启力(非淹没)小于门重1/5，带缓冲装置","套",{"v":2,"d":"2.00"}]
["三","高压及强电设备"]
[1,"TM1主变压器","SCB18-800/10，800KVA(全铜绕组带不锈钢外壳)","台",{"v":1,"d":"1.00"}]
[2,"TM2站用变压器","SCB18-100/10，100KVA(全铜绕组带不锈钢外壳)","台",{"v":1,"d":"1.00"}]
[3,"10KV高压进线柜","KYN28A-12(800x1500x2260mm)含微机保护装置，备自投切换装置","面",{"v":2,"d":"2.00"}]
[4,"1OKV高压计量柜","KYN28A-12(800x1500x2260mm)","面",{"v":2,"d":"2.00"}]
[5,"10KV变压器出线柜","KYN28A-12(800x1500x2260mm)含微机保护装置","面",{"v":2,"d":"2.00"}]
[6,"TM1低压考核柜","GCK(800x800x2260mmm)","面",{"v":1,"d":"1.00"}]
[7,"TM1低压受电柜","GCK(800x800x2260mm)","面",{"v":1,"d":"1.00"}]
[8,"TM1电容补偿柜","GCK(800x800x2260mm)","面",{"v":1,"d":"1.00"}]
[9,"低压移磁无级调压启动装置","RYZQ-D-280KW/380V(800x800x2260mm","面",{"v":2,"d":"2.00"}]
[10,"TM2低压考核柜","GCK(800x800x2260mm)","面",{"v":1,"d":"1.00"}]
[11,"TM2双电源转换柜","GCK(800x800x2260mm)","面",{"v":1,"d":"1.00"}]
[12,"TM2电容补偿柜(40kvar)","GCK(800x800x2260mm)","面",{"v":1,"d":"1.00"}]
[13,"TM2低压出线柜","GCK(800x800x2260mm)","面",{"v":2,"d":"2.00"}]
[14,"静音型柴油发电机组","80kW.O.4KV.柴油发电机组、静音外壳、控制箱。蓄电池。消声器防震胶、排风槽、排风百叶密及必需附件等、带自启动功能。","台",{"v":1,"d":"1.00"}]
[15,"直流电源屏","220V，65AH，800×800×2260mm","套",{"v":1,"d":"1.00"}]
[16,"泵房动力配电箱","380/220V，304不锈钢外壳，挂墙安装","个",{"v":1,"d":"1.00"}]
[17,"防洪水闸动力配电箱","380/220V，304不锈钢外壳，挂墙安装","个",{"v":1,"d":"1.00"}]
[18,"防洪闸门启闭机控制箱","380/220V，控制1台启闭机7.5kW，304不锈钢外壳，挂墙安装","个",{"v":2,"d":"2.00"}]
[19,"自排闸门启闭机控制箱","380/220V，控制1台启闭机11kW，304不锈钢外壳，挂墙安装","个",{"v":1,"d":"1.00"}]
[20,"抓斗清污机控制箱","380/220V，控制1台启闭机7.5kW，304不锈钢外壳，挂墙安装","个",{"v":1,"d":"1.00"}]
[21,"电机加热器控制箱","380/220V，控制2合电机加热器2x2KW，304不锈钢外壳，挂墙安装","个",{"v":1,"d":"1.00"}]
[22,"风机控制箱","380/220V，控制8合风机机8x0.25kW，304不锈钢外壳，挂安装","个",{"v":1,"d":"1.00"}]
[23,"泵房起重机现场开关箱","380/220V，304不锈钢外壳，户内挂墙安装","个",{"v":1,"d":"1.00"}]
[24,"检修闸门电动葫芦开关箱","380/220V，304不锈钢外壳，户内挂墙安装","个",{"v":1,"d":"1.00"}]
[25,"照明配电箱","380/220V,定制","个",{"v":2,"d":"2.00"}]
[26,"低噪音轴流风机","（带防虫防雨罩） CDZ-4-0.25kW-4P,3785m3/h，壁装","台",{"v":8,"d":"8.00"}]
[27,"火灾自动报警成套装置","含火灾自动报警控制器1台,感温感烟探测器各1个，声光报警器各1个及配套缆线","套",{"v":1,"d":"1.00"}]
[28,"10kV自动化分接箱","二进二出","套",{"v":2,"d":"2.00"}]
["四","信息化系统设备"]
[1,"不间断电源UPS(含后备电池组)","容量：6kVA/2h，工作方式：在线式；输入：~380V；RS485通讯，主机与电池整合进柜，尺寸600X800X2260(宽x深x高)，含柜内辅材、风扇、温湿度控制器。含配电箱。","套",{"v":1,"d":"1.00"}]
[2,"网络柜","尺寸600×800×2260(宽×深×高),前后开门下进线，2mm厚冷轧板,含柜内辅材、风扇、温湿度控制器 380/220V 11出线","套",{"v":1,"d":"1.00"}]
[3,"控制台","长×宽×高=2000×1200×750mm，防火实木板材制作","套",{"v":1,"d":"1.00"}]
[4,"控制台座椅","真皮，铝合金脚","张",{"v":2,"d":"2.00"}]
[5,"闸门开度仪","范围：0-8m，分辨率：1mm，传感器：多圈绝对型光电编码器，配套显示仪，带RS485接口","个",{"v":3,"d":"3.00"}]
[6,"闸门荷重仪","HZY-3型；测量范围：0~300KN；分辨率：0.01KN；精度：±0.1%F·S±0.1KN","个",{"v":3,"d":"3.00"}]
[7,"行程开关","LXK4-048/1(3常闭3常开)","个",{"v":6,"d":"6.00"}]
[8,"一杆式水位雨量视频监测站","包括：30米量程水位计1个；0.5m量程翻斗式雨量计1个：遥测终端RTU1个；遥测终端箱1个；5m监测立杆及基础1根等","套",{"v":1,"d":"1.00"}]
[9,"一杆式水位视频监测站","包括：30米量程水位计1个；遥测终端RTU1个；遥测终端箱1个；5m监测立杆及基础1根等","套",{"v":1,"d":"1.00"}]
[10,"工业级交换机","24个10/100/1000Base-T自适应电口，交换容量>336Gbps/3.36Tbps，支持全端口线速转发；支持终端识别、终端准入、安全防护；支持胖瘦一体化","台",{"v":1,"d":"1.00"}]
[11,"视频监控操作员站","11代i7-11700F16G1T+256GRX550X4G独显win11)23英寸","套",{"v":1,"d":"1.00"}]
[12,"视频监控管理服务器","R740服务器主机/2*至强银牌4210R十核2.4GHz/16G*4/4TSAS*3/H730P-2G/750W双电/导轨/三年保修","套",{"v":1,"d":"1.00"}]
[13,"NVR硬盘录像机(24路）","硬件规格：3U标准机架式；2个HDMI，2个VGA，HDMI+VGA组内同源；16盘位，可满配8T、10T硬盘，支持硬盘热插拔；2个千兆网口、2个USB2.0接口、1个USB3.0接口、1个eSATA接口；支持RAID0、1、5、10，支持全局热备盘","台",{"v":1,"d":"1.00"}]
[14,"4TB企业级硬盘","容量：4T，接口类型：SATA，接口速率：6Gb/s","个",{"v":7,"d":"7.00"}]
[15,"前端安装箱","350x350x200，IP54，SS3041.5mm厚","个",{"v":16,"d":"16.00"}]
[16,"电源防雷器","Uc≥AC/DC28V，Up≤1.5kV，Iimp>20KA(I类试验)","个",{"v":16,"d":"16.00"}]
[17,"信号防雷器","Uc>6V，155MHz，Iimp>2.5KA(I类试验)","个",{"v":16,"d":"16.00"}]
[18,"摄像机电源","DC24V开关电源","个",{"v":16,"d":"16.00"}]
[19,"广播网关","参考型号E-PA3，远程广播网关","个",{"v":1,"d":"1.00"}]
[20,"调度中心寻呼主机","E-A32i，配备鹅颈麦克风，功能强大。","个",{"v":1,"d":"1.00"}]
[21,"压电式加速度传感器","VS-025，灵敏度：100mV/g，频响范围：0.5Hz～14000Hz(±3dB），加速度范围：±80gpeak，温度响应：-50°C～121°C，供电电压：18～30VDC，外壳材质：不锈钢。","个",{"v":8,"d":"8.00"}]
[22,"电涡流摆度传感器","TS-CWY-D0，探头直径：Φ8mm，线性范围：8mm，灵敏度：8.0V/mm±4%，线性度：系统误差≤±1%，频响特性：0～10KHz，配5米电缆。","套",{"v":4,"d":"4.00"}]
[23,"转速传感器","RS-02，测量范围：0～20000个脉冲/秒，测量精度：±1个脉冲/秒，安装距离：0.5～4mm，响应频率：1Hz～20KHz，输出方式：PNP开路输出。","个",{"v":2,"d":"2.00"}]
[24,"压力变送器","测量范围：-0.1～0.1MPa，测量精度：≤±0.15%FS，配5米电缆。","个",{"v":2,"d":"2.00"}]
[25,"数据采集单元","1路通道，RS-485通讯口","台",{"v":14,"d":"14.00"}]
[26,"压力显示仪","压力变送器配套","台",{"v":2,"d":"2.00"}]
[27,"在线状态监测装置","输入信号：振动、摆度、转速、压力等传感器，12通道，10.2英寸真彩色触摸屏显示，测量精度：%%P0．5级，线性误差≤1%FS（满量程），以太网接口","台",{"v":2,"d":"2.00"}]
[28,"机组在线监测箱","每台机组设1个在线监测箱，材质：304不锈钢","套",{"v":2,"d":"2.00"}]
[29,"渗压计","型式：振弦式；量程：0.35Mpa；分辨率：0.025%FS；精度：0.1%FS","套",{"v":12,"d":"12.00"}]
[30,"现地控制单元(MCU)","10通道","台",{"v":2,"d":"2.00"}]
[31,"工程安全监测专业分析评价软件","软件具有数据管理、分析、报警、图形界面展示、预测评价等功能","套",{"v":1,"d":"1.00"}]
[null,"总合计"]
["注：1、单价包含材料费（包含配套材料、辅助材料等）、人工费、机械费、制作安装费、试验检测费、包装费、运杂费（包括装卸车费）、培训费、保险费、缺陷修复费、综合管理费、技术资料费、风险费、利润、税费（13%）、政策性文件规定费用等一切费用，即货物到达交货地点所发生的一切费用；数量以采购人实际采购数量为准，经验收合格后按送货量月结80%（进度款到账的情况下），当年结算至实际供货量的97%，实际供货款的3%作为质保金，质保金待完工一年后付清，具体以签订的合同条款为准。\n2、供应商可选择其中一项或多项报价，未报价设备单价用“/”填写。\n3、以上清单项目特征以施工图纸及答疑回复为准。（邹工：13480512816）"]
["供应商名称："]
["供应商地址："]
["联系人："]
["联系电话："]
["日期："]