{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["钢管","球墨铸铁管"],"not_rendered":{"external_links":1,"defined_names":4},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"钢管","index":0,"n_rows":24,"n_cols":7,"rows_kept":24,"merged":[[0,0,0,1],[1,0,1,6],[2,0,2,6],[4,3,17,3],[18,0,18,6],[19,0,19,5],[20,0,20,5],[21,0,21,5],[22,0,22,5],[23,0,23,5]],"flags":["formulas_cached_only"]}
["附件"]
["惠州市水电建筑工程有限公司2026年度第一批次焊接钢管采购项目询价报价表"]
["类别：焊接钢管"]
["序号","材料名称","规格型号或指标","技术参数","单位","报价（元）","备注"]
[1,"焊接钢管","D1420×14","1、焊接直缝钢管，材质为Q235B，构件（如排气阀与闸阀）中间采用钢管连接；\n2、钢管之间、钢管与弯头之间采用焊接，钢管与闸阀、与PE管之间采用法兰连接；\n3、防腐材料：油漆：内漆外漆采用GZ-2防腐涂料衬涂；纤维布采用玻璃纤维布。\n（1）开挖段埋地管道外壁防腐（四油二布），先刷一道，缠绕玻璃纤维布一层，再涂底漆一道，再缠绕玻璃纤维布一层，再涂面漆二道。干膜厚度大于400um。管道内壁防腐（二底二面），先刷底漆2道，面漆2道，2道底漆干膜厚度大于100um，2道面漆干膜厚度大于100um，总干膜厚度大于200um。\n（2）架空管、明敷段、顶管段管道外壁防腐（六油二布），面料二道－玻璃布－面料二道－玻璃布－面料二道，干膜厚度大于600um，接口处按照《管道外防腐补口技术规范》（GB/T51241-2017）要求执行；钢管内壁防腐采用GZ－2（0710）新型高分子防腐涂料，做法根据产品要求而定，产品须经国家卫生部门批准的无毒性材料。","m",null,"顶管"]
[2,"焊接钢管","D1220×14",null,"m",null,"顶管"]
[3,"焊接钢管","D1220×12",null,"m",null,"顶管"]
[4,"焊接钢管","D1020×10",null,"m",null,"开挖"]
[5,"焊接钢管","D820×12",null,"m",null,"顶管"]
[6,"焊接钢管","D820×10",null,"m",null,"开挖"]
[7,"焊接钢管","D630×12",null,"m",null,"牵引"]
[8,"焊接钢管","D630×10",null,"m",null,"开挖"]
[9,"焊接钢管","D530×10",null,"m",null,"开挖"]
[10,"焊接钢管","D426×9",null,"m",null,"开挖"]
[11,"焊接钢管","D325×8",null,"m",null,"开挖"]
[12,"焊接钢管","D219×6",null,"m",null,"开挖"]
[13,"焊接钢管","D159×4.5",null,"m",null,"开挖"]
[14,"焊接钢管","D108×4",null,"m",null,"开挖"]
["注：单价包含材料费（包含配套材料、辅助材料等，如钢管现场焊接施工所需的防腐材料）、人工费、机械费、制作费、试验检测费、包装费、运杂费（包括装卸车费）、培训费、保险费、缺陷修复费、综合管理费、技术资料费、风险费、利润、各种税费、政策性文件规定费用等一切费用，即货物到达交货地点所发生的一切费用；数量以采购人实际采购数量为准，经验收合格后按送货量月结80%（进度款到账的情况下），当年结算至实际供货量的97%，实际供货款的3%作为质保金，质保金待完工一年后付清，具体以签订的合同条款为准。"]
["供应商名称："]
["供应商地址："]
["联系人："]
["联系电话："]
["日    期："]

{"sheet":"球墨铸铁管","index":1,"n_rows":17,"n_cols":7,"rows_kept":17,"merged":[[0,0,0,1],[1,0,1,6],[2,0,2,6],[4,3,10,3],[11,0,11,6],[12,0,12,5],[13,0,13,5],[14,0,14,5],[15,0,15,5],[16,0,16,5]],"flags":["formulas_cached_only"]}
["附件"]
["惠州市水电建筑工程有限公司2026年度第一批次球墨铸铁管采购项目询价报价表"]
["类别：球墨铸铁管"]
["序号","材料名称","规格型号或指标","技术参数","单位","报价（元）","备注"]
[1,"球墨铸铁管","DN600","1、球墨铸铁管采用T型承插离心球墨铸铁管材（可切割），每节长6m，管道工作压力为1.0Mpa，壁厚等级为K9,球墨铸铁按国标《水及燃气用球墨铸铁管、管件和附件（GB/T 13295-2003）》执行。\n2、球墨铸铁管之间采用T型橡胶圈承插连接，球墨铸铁管与闸阀等构件的连接采用盘承直管及盘插直管连接。\n3、球墨铸铁管壁厚级别K9级，内涂层为硅酸盐水泥砂浆，外涂层为金厘锌(含锌量9996)及沥青。","m",null,"含橡胶圈，开挖"]
[2,"球墨铸铁管","DN500",null,"m",null,"含橡胶圈，开挖"]
[3,"球墨铸铁管","DN400",null,"m",null,"含橡胶圈，开挖"]
[4,"球墨铸铁管","DN300",null,"m",null,"含橡胶圈，开挖"]
[5,"球墨铸铁管","DN200",null,"m",null,"含橡胶圈，开挖"]
[6,"球墨铸铁管","DN150",null,"m",null,"含橡胶圈，开挖"]
[7,"球墨铸铁管","DN100",null,"m",null,"含橡胶圈，开挖"]
["注：单价包含材料费（包含配套材料、辅助材料等，如钢管现场焊接施工所需的防腐材料）、人工费、机械费、制作费、试验检测费、包装费、运杂费（包括装卸车费）、培训费、保险费、缺陷修复费、综合管理费、技术资料费、风险费、利润、各种税费、政策性文件规定费用等一切费用，即货物到达交货地点所发生的一切费用；数量以采购人实际采购数量为准，经验收合格后按送货量月结80%（进度款到账的情况下），当年结算至实际供货量的97%，实际供货款的3%作为质保金，质保金待完工一年后付清，具体以签订的合同条款为准。"]
["供应商名称："]
["供应商地址："]
["联系人："]
["联系电话："]
["日    期："]